## Non-Resi ASHP
NYS Clean Heat
Con Edison Heat Pump Program
Non-Residential ASHP Programs
Standards and Quality Assurance ¹
Version 2025.1
Protocol for Immediate Safety Concerns ² • The inspector should notify the customer concerning any Immediate Safety Concern finding and emphasize that these conditions must be urgently addressed. • The Inspector should then notify their management, Con Edison, and the Participating Contractor. • Con Edison requires Participating Contractors to address such concerns immediately, and at all times as soon as reasonably practicable, with an expectation of within 24-hours of notice if the facts and circumstances allow.
| # | Objective / Task Description
All Projects | C1 | Verify installed equipment is as proposed on application, quantity, make and model.
| C1A | Typos on any project documentation for model or serial numbers that do not impact sizing or equipment eligibility.
| C5 | Verify site conditions are consistent with Load Sizing Analysis or a revised energy analysis has been completed. Review of ACCA (Manual D, J, N or S) or other approved load calculation methodologies, with observed site conditions. Not Applicable For C&I Projects
| C15B | Verify that units are above snow depth level according to ACCA Weather Station data as provided by the NYS Clean Heat program. Only applicable to ASHP applications
| C17 | Observe functional testing of equipment in either cooling or heating mode as conducted by contractor or operator, if conditions allow.
| C18 | Verify that electrical disconnect is installed in an accessible location for service.
Existing Buildings Only
Decommissioning Only | DE2 | Confirm the contractor-completed Decommissioning Checklist matches conditions on site.
| DE2A | Conditions on site have fully met requirements in Decommissioning Checklist but the checklist itself was filled out incorrectly.
Decommissioning Verification | DV1 | NATURAL GAS ONLY: On the day of the inspection, visually verify that visible fuel line(s) to the decommissioned appliance have been disconnected, removed, and capped with a press fitting or a threaded fitting using thread sealant, fuel line cap is tight and secure, and that no odor or sound of leaking gas is detected.
| DV2 | OIL OR PROPANE ONLY: On the day of the inspection, visually verify oil fuel lines to decommissioned appliance(s) have been disconnected, removed and capped using a threaded fitting and that the cap is tight and secure. Additionally, visually verify that oil or propane is not leaking.
| DV3 | Verify disconnection of power supply to decommissioned space heating appliance. (E.g. Visually verify that no exposed wires can be seen, etc).
| DV4 | Visually verify that a Carbon Monoxide detector is present and functioning.
Venting | V1 | Visually verify that rigid metal caps with threaded fasteners have been used to seal flue vents previously used by the decommissioned appliance(s).
| V2 | For commonly vented systems with an operational DHW or combustion appliance, confirm that the remaining vent is free of visible defects, pitched upward toward the chimney, and supported.
¹ Critical buildings may be exempt from decommissioing requirements. See Con Edison Clean Heat Program Manual for details. 2 Immediate safety concerns include, but are not limited to, leaks (e.g. natural gas, propane or oil), unsecured fuel lines or eletrical disconnects, ventilation issues, and other potential hazards.