## AWHP Checklist
NYS Clean Heat Statewide Heat Pump Program
Standards and Quality Assurance
Air to Water Heat Pump Checklist
Updated: 9/1/2025
# | Applicable System Type | Category | Objective / Task Description | Criteria | Document Required / Verification Method | Responsible Party | Program Phase | Defect Category | Reference
DMH1 | Hydro-Split Monobloc | Design | Verify if a startup checklist was provided, that contained the following elements (n/a for DX split systems) 1. Antifreeze type and concentration documentation. 2. Burst temperature documentation. Burst temperature must be at least 10°F lower than the 99% outdoor air heating design temperature. 3. Load side leak test and test method documentation (downstream piping). 4. Source side leak test and test method documentation (upstream piping). 4. Water source, water quality testing, water treatement method documentation. 5. Water to water heat exchanger temperature and pressure differential test documentation (only applicable if W2W HEX exists). 6. Flushing procedure documentation. 7. Purging procedure documentation. 8. Functional testing with space setpoint temperature, outdoor air temperature, system flow rate, leaving water temperature documented in both heating and cooling mode as conditions allow. | Document Review | Startup checklist | Participating Contractor | Construction | Major
DDX1 | DX split | Design | Verify if a startup checklist was provided, that contained the following elements (n/a for monobloc or hydro-split systems) Refrigerant Loop Side Checks 1. Documentation that the system was vacuumed down to 500 microns or less. 2. Documentation of the refrigerant volume used to charge the system. 3. Documentation of the Actual and Target Superheat (°F) or the Actual and Target Subcooling (°F). 4. Documentation of condensate drain function testing 5. Documentation of functional testing in heating and cooling modes 6. Air filter installation verification if applicable Hydronic Side Checks 1. Load side leak test and test method documentation (downstream piping). 2. Water source, water quality testing, water treatement method documentation. 3. Flushing procedure documentation. 4. Purging procedure documentation. 5. Functional testing with space setpoint temperature, outdoor air temperature, system flow rate, leaving water temperature documented in both heating and cooling mode as conditions allow. | Document Review | Startup checklist | Participating Contractor | Construction | Major
D2 | All | Design | Verify design schematic and sequence of operations documentation have been provided. | Document Review | Design schematic and sequence of operations | Participating Contractor | Design | Major
D3 | All | Design | Verify the Sizing and Design Calculator is complete and is consistent with site conditions. Verify the total AWHP equipment heating load ratio and room by room heating load ratios are within 90 to 120%. | Document Review | Sizing and Design Calculator (Prescriptive Incentive Calculator) | Participating Contractor | Design | Major
C1 | All | Installation | Verify installed equipment is as proposed on the invoice or application documentation, including quantity, make and model information. | Visual Observation / Photo Documentation | Invoice, application, and equipment specification | Participating Contractor | Construction | Major
C2 | All | Installation | Verify installed system matches the design schematic to ensure proper operation and functions in accordance with the sequence of operations. | Visual Observation | Design schematic and sequence of operations | Participating Contractor | Construction | Major
C3 | All | Installation | Verify outdoor unit, indoor unit, tanks, heat exchangers, and pump connections (if applicable) are leak free. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major
C4 | All | Installation | Verify that safe access to the site and associated equipment has been provided | Situational Awareness | Visual Observation / Photo Documentation | Participating Contractor | Construction | Critical
C5 | All | Installation | Verify site conditions are consistent with the submitted Load Sizing Analysis, and that the analysis used an ACCA approved Manual J software platform or received a program exception. | Visual Observation / Document Review | Design report referencing ACCA Manual J or other approved heating and cooling calculation methodologies / Site observation | Participating Contractor | Design | Major | NYC DOB EN2: As Built Energy Analysis https://www.acca.org/standards/approved-software
C6 | All | Installation | Verify that the first 6' of hydronic heating circulation piping from the indoor unit/storage tank to the heat emitters are insulated. Verify that any exposed hot water lines are not in direct contact, regardless of material. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major
C7 | All | Installation | Verify that the hydronic cooling lines from the indoor unit/storage tank to terminal units are insulated and vapor sealed. Verify that any exposed cold water lines are not in direct contact, regardless of material. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major
C8 | Hydro-Split Monobloc | Installation | Verify that the outdoor hydronic piping is either insulated with freeze protection or heat trace is installed. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major
C9 | All | Installation | Verify that exposed new or retrofitted ductwork is properly sealed and insulated if located outside the building's thermal envelope. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major
C10 | All | Installation | In areas formerly heated, directly or indirectly, by a fossil fuel heating system, confirm that any plumbing outside the thermal envelope is adequately protected from freezing by insulation, heat, or both. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major
C11 | All | Installation | Verify temperature and pressure relief valve are installed on any pressure tanks and that the relief valve terminates within 6" of the floor. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Critical
C12 | All | Installation | Verify all exposed equipment and pipe supports appear to be properly secured. | Visual Observation / Photo Documentation | Visual Observation / Photo Documentation | Participating Contractor | Construction | Major
C13 | All | Installation | Verify outdoor unit is installed with sufficient clearances per manufacturer's requirements. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major
C14 | All | Installation | Observe condensate and defrost lines where accessible for leaks. Confirm condensate/defrost lines terminate in either a domestic drain before a trap or external location. Defrost must not drain onto other heat pumps or where refreeze will occur on walking surfaces. Condensate must not drain onto an external stairway. Condensate and defrost drainage must flow freely. Confirm with the homeowner that there is no indication of condensate line leakage before the termination point. | Visual Observation / Photo Documentation / Customer Confirmation | Site Observation / Customer Confirmation | Participating Contractor | Construction | Major
C14B | All | Installation | Confirm condensate and defrost lines do not terminate in any of the following locations: Drain, waste, vent (DWV) lines after traps, directly against wood walls or structural components, within the line hide, onto a flat surface that has no drainage, or to other locations that would likely cause property damage or occupant danger. | Visual Observation / Photo Documentation / Customer Confirmation | Site Observation / Customer Confirmation | Participating Contractor | Construction | Minor | International Mechanical Code Chapter 11 - CODE: 307.2.1.1 Condensate discharge
C15 | All | Installation | Observe that the outdoor unit is away from or protected from increased sources of water/ice/snow from above (i.e. more than normal precipitation, e.g. beneath drip edge, beneath snow-slide, beneath another heat pump, etc.). The presence of gutters does provide sufficient protection for asphalt roofs. The presence of gutters does not provide sufficient protection for all other pitched roof types. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major
C15B | All | Installation | Verify that units are above snow depth level according to ACCA Weather Station data as provided by the NYS Clean Heat program. | Visual Observation / Photo Documentation | Site Observation / Measurement and Photo Documentation | Participating Contractor | Construction | Major
C16 | All | Installation | Verify outdoor unit is installed level. | Visual Observation / Photo Documentation | Site Observation / Measurement and Photo Documentation | Participating Contractor | Construction | Major
C16B | All | Installation | If unit is connected to the building's framing (e.g. wall mounted, or on a connected deck), vibration dampeners are installed. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major
C17 | All | Installation | Observe functional testing of equipment in either cooling or heating mode as conducted by contractor or operator, if conditions allow. | Functional Test | Site Observation / Photo Documentation | Participating Contractor | Construction | Major | C. McCracken / CLEAResult, 2016
C18 | All | Installation | Verify that electrical disconnect is installed in an accessible location for service. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major | 2020 NFPA 70 / NEC 2020
C19 | (Intentionally Blank)
C20 | All | Installation | Verify all exterior penetrations, for pipes, linesets, electrical, or otherwise, are properly sealed. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major
CDX1 | DX split | Installation | Sample for refrigerant leaks at exposed field connections | Functional Test | Refrigerant detector | Participating Contractor | Construction | Critical
CDX2 | DX split | Installation | Verify all accessible refrigerant line (indoor and outdoor) set is insulated. Verify that all outdoor refrigerant line set is protected from UV. To comply, no more than 12" of any accessible refrigerant line may be left un-insulated/protected from UV at the outdoor unit connection. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major | NYC 1RCNY 5000- 01
CDX2B | DX split | Installation | Verify no more than 1" of any refrigerant line is unprotected at the outdoor unit connection. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Minor | NYC 1RCNY 5000- 01
O1 | All | Operation | Verify approval of work in accordance with applicable codes and local requirements. | Document Review | Project Application Document Attestation | Participating Contractor | Construction | Critical
O2 | All | Operation | Verify Manufacturer's Warranty has been provided to owner. | Document Review | Manufacturers Warranty | Participating Contractor | Occupancy | Minor
O3 | All | Operation | Confirm customer/ operator has been provided with training on operation of system. | Document Review | Product Manual w/ Operating Instructions / Homeowner Confirmation | Participating Contractor | Occupancy | Major
O4 | All | Operation | Confirm that the system owners manual and maintenance instructions are available on site. | Document Review | Product Manual w/ Maintenance Instructions / Homeowner Confirmation | Participating Contractor | Occupancy | Minor
O5 | All | Operation | If fossil fuel heating system exists and is operational, verify the AWHP is used as the primary source of heating and/or cooling year round. Verify the fossil fuel heat source is only a backup and controlled to operate in emergency situations when the AWHP is non-operational. | Homeowner Confirmation / Visual Observation | Homeowner Confirmation / Visual Observation | Participating Contractor | Occupancy | Major
O6 | All | Operation | Confirm the distribution system is capable of providing sufficient comfort to all spaces conditioned by the heat pump unit(s). | Homeowner Confirmation / Visual Observation | Homeowner Confirmation / Visual Observation / Photo Documentation | Participating Contractor | Occupancy | Major

## Sheet1
Site Observation / Photo Documentation
Site Observation
Refrigerant detector
Manufacturers Warranty
Approved construction documents
Contractor Attestation
Document Review
Functional Test
quantity of heat emitters
type of heat emitters
pumping power
total heating load of the house at design conditions
heated square footage
estimate Btu/sq ft