| 14610 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14610
| 14611 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14611
| 14612 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14612
| 14613 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14613
| 14614 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14614
| 14615 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14615
| 14616 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14616
| 14617 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14617
| 14618 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14618
| 14619 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14619
| 14620 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14620
| 14621 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14621
| 14622 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14622
| 14623 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14623
| 14624 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14624
| 14625 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14625
| 14626 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14626
| 14627 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14627
| 14638 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14638
| 14639 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14639
| 14642 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14642
| 14643 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14643
| 14644 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14644
| 14646 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14646
| 14647 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14647
| 14649 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14649
| 14650 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14650
| 14651 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14651
| 14652 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14652
| 14653 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14653
| 14692 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14692
| 14694 | GREATER ROCHESTER INTL | Rochester | 6.6 | 86 | 12 | 14694
| 14701 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14701
| 14702 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14702
| 14706 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14706
| 14707 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14707
| 14708 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14708
| 14709 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14709
| 14710 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14710
| 14711 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14711
| 14712 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14712
| 14714 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14714
| 14715 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14715
| 14716 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14716
| 14717 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14717
| 14718 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14718
| 14719 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14719
| 14720 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14720
| 14721 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14721
| 14722 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14722
| 14723 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14723
| 14724 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14724
| 14726 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14726
| 14727 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14727
| 14728 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14728
| 14729 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14729
| 14730 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14730
| 14731 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14731
| 14732 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14732
| 14733 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14733
| 14735 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14735
| 14736 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14736
| 14737 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14737
| 14738 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14738
| 14739 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14739
| 14740 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14740
| 14741 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14741
| 14742 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14742
| 14743 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14743
| 14744 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14744
| 14745 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14745
| 14747 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14747
| 14748 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14748
| 14750 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14750
| 14751 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14751
| 14752 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14752
| 14753 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14753
| 14754 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14754
| 14755 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14755
| 14756 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14756
| 14757 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14757
| 14758 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14758
| 14760 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14760
| 14766 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14766
| 14767 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14767
| 14769 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14769
| 14770 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14770
| 14772 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14772
| 14774 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14774
| 14775 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14775
| 14777 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14777
| 14778 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14778
| 14779 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14779
| 14781 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14781
| 14782 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14782
| 14783 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14783
| 14784 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14784
| 14785 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14785
| 14786 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14786
| 14787 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14787
| 14788 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14788
| 14801 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14801
| 14802 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14802
| 14803 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14803
| 14804 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14804
| 14805 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14805
| 14806 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14806
| 14807 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14807
| 14808 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14808
| 14809 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14809
| 14810 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14810
| 14812 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14812
| 14813 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14813
| 14814 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14814
| 14815 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14815
| 14816 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14816
| 14817 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14817
| 14818 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14818
| 14819 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14819
| 14820 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14820
| 14821 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14821
| 14822 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14822
| 14823 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14823
| 14824 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14824
| 14825 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14825
| 14826 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14826
| 14827 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14827
| 14830 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14830
| 14831 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14831
| 14836 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14836
| 14837 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14837
| 14838 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14838
| 14839 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14839
| 14840 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14840
| 14841 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14841
| 14842 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14842
| 14843 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14843
| 14845 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14845
| 14846 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14846
| 14847 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14847
| 14850 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14850
| 14851 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14851
| 14852 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14852
| 14853 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14853
| 14854 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14854
| 14855 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14855
| 14856 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14856
| 14857 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14857
| 14858 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14858
| 14859 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14859
| 14860 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14860
| 14861 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14861
| 14863 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14863
| 14864 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14864
| 14865 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14865
| 14867 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14867
| 14869 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14869
| 14870 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14870
| 14871 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14871
| 14872 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14872
| 14873 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14873
| 14874 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14874
| 14876 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14876
| 14877 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14877
| 14878 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14878
| 14879 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14879
| 14880 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14880
| 14881 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14881
| 14882 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14882
| 14883 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14883
| 14884 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14884
| 14885 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14885
| 14886 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14886
| 14887 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14887
| 14889 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14889
| 14891 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14891
| 14892 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14892
| 14893 | GREATER BINGHAMTON AP | Binghamton | 3.9 | 82.3 | 12 | 14893
| 14894 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14894
| 14895 | BUFFALO NIAGARA INTL | Buffalo | 6.8 | 83.9 | 18 | 14895
| 14897 | CHAUTAUQUA COUNTY AP | Jamestown | 4.5 | 81.1 | 12 | 14897
| 14898 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14898
| 14901 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14901
| 14902 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14902
| 14903 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14903
| 14904 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14904
| 14905 | ELMIRA CORNING REGIONAL | Elmira | 4.1 | 86.5 | 6 | 14905
Note on L4: ASHRAE 2017

## Building Profiles (hidden)
Building Type |  | Schedules (ASHRAE 90.1 User Manual Typical Load Profiles) |  | Office |  |  | Assembly |  |  | Health |  |  | Light Manufacturing |  |  | Restaurant |  |  | Retail |  |  | School |  |  | Warehouse |  |  | Laboratory |  |  | Hotel |  |  | Residential |  |  | Multi-Family |  |  | Custom
Office | 1 |  | Hour (Time of Day) | HVAC Schedule |  |  | HVAC Schedule |  |  | HVAC Schedule |  |  | HVAC Schedule |  |  | HVAC Schedule |  |  | HVAC Schedule |  |  | HVAC Schedule |  |  | HVAC Schedule |  |  | HVAC Schedule |  |  | HVAC Schedule |  |  | HVAC Schedule |  |  | HVAC Schedule |  |  | HVAC Schedule
Assembly | 2 |  |  | Weekday | Sat | Sunday | Weekday | Sat | Sunday | Weekday | Sat | Sunday | Weekday | Sat | Sunday | Weekday | Sat | Sunday | Weekday | Sat | Sunday | Weekday | Sat | Sunday | Weekday | Sat | Sunday | Weekday | Sat | Sunday | Weekday | Sat | Sunday | Weekday | Sat | Sun | Weekday | Sat | Sun | Weekday | Sat | Sunday
Health | 3 |  | 1:00 | Off | Off | Off | Off | Off | Off | On | On | On | Off | Off | Off | On | On | On | Off | Off | Off | Off | Off | Off | Off | Off | Off | On | On | On | On | On | On | On | On | On | On | On | On | 0 | 0 | 0
Light Manufacturing | 4 |  | 2:00 | Off | Off | Off | Off | Off | Off | On | On | On | Off | Off | Off | On | On | On | Off | Off | Off | Off | Off | Off | Off | Off | Off | On | On | On | On | On | On | On | On | On | On | On | On | 0 | 0 | 0
Restaurant | 5 |  | 3:00 | Off | Off | Off | Off | Off | Off | On | On | On | Off | Off | Off | On | On | On | Off | Off | Off | Off | Off | Off | Off | Off | Off | On | On | On | On | On | On | On | On | On | On | On | On | 0 | 0 | 0
Retail | 6 |  | 4:00 | Off | Off | Off | Off | Off | Off | On | On | On | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off | On | On | On | On | On | On | On | On | On | On | On | On | 0 | 0 | 0
School | 7 |  | 5:00 | Off | Off | Off | Off | Off | Off | On | On | On | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off | On | On | On | On | On | On | On | On | On | On | On | On | 0 | 0 | 0
Warehouse | 8 |  | 6:00 | On | On | Off | On | Off | Off | On | On | On | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off | On | On | On | On | On | On | On | On | On | On | On | On | 0 | 0 | 0
Laboratory | 9 |  | 7:00 | On | On | Off | On | On | On | On | On | On | On | On | Off | Off | Off | Off | On | On | Off | Off | Off | Off | Off | Off | Off | On | On | On | On | On | On | On | On | On | On | On | On | 0 | 0 | 0
Hotel | 10 |  | 8:00 | On | On | Off | On | On | On | On | On | On | On | On | Off | On | Off | Off | On | On | Off | On | Off | Off | On | Off | Off | On | On | On | On | On | On | On | On | On | On | On | On | 0 | 0 | 0
Residential | 11 |  | 9:00 | On | On | Off | On | On | On | On | On | On | On | On | Off | On | Off | Off | On | On | On | On | On | Off | On | On | Off | On | On | On | On | On | On | Off | On | On | Off | On | On | 0 | 0 | 0
Multifamily | 12 |  | 10:00 | On | On | Off | On | On | On | On | On | On | On | On | Off | On | On | Off | On | On | On | On | On | Off | On | On | Off | On | On | On | On | On | On | Off | On | On | Off | On | On | 0 | 0 | 0
Custom | 13 |  | 11:00 | On | On | Off | On | On | On | On | On | On | On | On | Off | On | On | On | On | On | On | On | On | Off | On | On | Off | On | On | On | On | On | On | Off | On | On | Off | On | On | 0 | 0 | 0
|  |  | 12:00 | On | On | Off | On | On | On | On | On | On | On | On | Off | On | On | On | On | On | On | On | On | Off | On | On | Off | On | On | On | On | On | On | Off | On | On | Off | On | On | 0 | 0 | 0
|  |  | 13:00 | On | On | Off | On | On | On | On | On | On | On | On | Off | On | On | On | On | On | On | On | On | Off | On | On | Off | On | On | On | On | On | On | Off | On | On | Off | On | On | 0 | 0 | 0
Multifamily |  |  | 14:00 | On | On | Off | On | On | On | On | On | On | On | On | Off | On | On | On | On | On | On | On | Off | Off | On | On | Off | On | On | On | On | On | On | Off | On | On | Off | On | On | 0 | 0 | 0
|  |  | 15:00 | On | On | Off | On | On | On | On | On | On | On | On | Off | On | On | On | On | On | On | On | Off | Off | On | On | Off | On | On | On | On | On | On | Off | On | On | Off | On | On | 0 | 0 | 0
|  |  | 16:00 | On | On | Off | On | On | On | On | On | On | On | On | Off | On | On | On | On | On | On | On | Off | Off | On | On | Off | On | On | On | On | On | On | On | On | On | On | On | On | 0 | 0 | 0
|  |  | 17:00 | On | On | Off | On | On | On | On | On | On | On | On | Off | On | On | On | On | On | On | On | Off | Off | On | Off | Off | On | On | On | On | On | On | On | On | On | On | On | On | 0 | 0 | 0
|  |  | 18:00 | On | Off | Off | On | On | On | On | On | On | On | On | Off | On | On | On | On | On | Off | On | Off | Off | Off | Off | Off | On | On | On | On | On | On | On | On | On | On | On | On | 0 | 0 | 0
|  |  | 19:00 | On | Off | Off | On | On | On | On | On | On | On | Off | Off | On | On | On | On | On | Off | On | Off | Off | Off | Off | Off | On | On | On | On | On | On | On | On | On | On | On | On | 0 | 0 | 0
|  |  | 20:00 | On | Off | Off | On | On | On | On | On | On | On | Off | Off | On | On | On | On | On | Off | On | Off | Off | Off | Off | Off | On | On | On | On | On | On | On | On | On | On | On | On | 0 | 0 | 0
|  |  | 21:00 | On | Off | Off | On | On | On | On | On | On | On | Off | Off | On | On | On | On | On | Off | On | Off | Off | Off | Off | Off | On | On | On | On | On | On | On | On | On | On | On | On | 0 | 0 | 0
|  |  | 22:00 | Off | Off | Off | On | On | On | On | On | On | On | Off | Off | On | On | On | Off | On | Off | On | Off | Off | Off | Off | Off | On | On | On | On | On | On | On | On | On | On | On | On | 0 | 0 | 0
|  |  | 23:00 | Off | Off | Off | On | On | On | On | On | On | Off | Off | Off | On | On | On | Off | Off | Off | Off | Off | Off | Off | Off | Off | On | On | On | On | On | On | On | On | On | On | On | On | 0 | 0 | 0
|  |  | 0:00 | Off | Off | Off | Off | Off | Off | On | On | On | Off | Off | Off | On | On | On | Off | Off | Off | Off | Off | Off | Off | Off | Off | On | On | On | On | On | On | On | On | On | On | On | On | 0 | 0 | 0
Balance Point (deg F)
|  |  | Building Profiles |  | Setpoints (deg F) |  |  |  | Existing Building |  |  |  | New Construction
[5 empty] | Occupied Hours |  | Unoccupied Hours |  | Occupied Hours |  | Unoccupied Hours |  | Occupied Hours |  | Unoccupied Hours
|  |  | Building Type |  | Cooling | Heating | Cooling | Heating | Cooling | Heating | Cooling | Heating | Cooling | Heating | Cooling | Heating
|  |  | Office | 1 | 75 | 70 | 78 | 67 | 57 | 53 | 60 | 50 | 54 | 51 | 57 | 48
|  |  | Assembly | 2 | 76 | 72 | 79 | 69 | 58 | 54 | 61 | 51 | 55 | 52 | 58 | 49
|  |  | Health | 3 | 76 | 72 | 79 | 69 | 58 | 54 | 61 | 51 | 55 | 52 | 58 | 49
|  |  | Light Manufacturing | 4 | 78 | 70 | 81 | 67 | 58 | 54 | 61 | 51 | 55 | 52 | 58 | 49
|  |  | Restaurant | 5 | 77 | 72 | 80 | 69 | 61 | 58 | 64 | 55 | 59 | 52 | 62 | 49
|  |  | Retail | 6 | 76 | 72 | 79 | 69 | 61 | 54 | 64 | 51 | 59 | 52 | 62 | 49
|  |  | School | 7 | 76 | 72 | 81 | 67 | 58 | 56 | 61 | 53 | 49 | 48 | 52 | 45
|  |  | Warehouse | 8 | 80 | 68 | 85 | 63 | 65 | 51 | 68 | 48 | 62 | 49 | 65 | 46
|  |  | Laboratory | 9 | 76 | 72 | 79 | 69 | 58 | 54 | 61 | 51 | 55 | 52 | 58 | 49
|  |  | Hotel | 10 | 76 | 72 | 81 | 67 | 52 | 51 | 55 | 48 | 52 | 50 | 55 | 47
|  |  | Residential | 11 | 75 | #N/A | 78 | #N/A | 58 | 60 | 61 | 57 | 63 | 55 | 66 | 52
|  |  | Multifamily | 12 | 75 | 70 | 78 | 67 | 58 | 60 | 61 | 57 | 63 | 55 | 66 | 52
|  |  | Custom | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Set Points are from Appendix A of TRM
Occupied Balance Points are from Geothermal Residential White Paper (2020) and ARUP Commercial Energy Plus Analysis where available; when building profile does not exist, value has been assumed.
Unoccupied Balance Points are Assumed, typ +/- 3 to 5 degrees of Occupied Balance Points
ARUP Commercial Analysis
[7 empty] | Balance Point COOLING |  |  |  | Balance Point HEATING
[7 empty] | Pre-1980 | Post-1980 | NC |  | Pre-1980 | Post-1980 | NC
|  |  | 4A | Academic | Academic | NY JFK | 56.76 | 56.9 | 50.53 |  | 53.84 | 53.16 | 52.55
|  |  | 5A | Academic |  | Buffalo | 57.35 | 57.37 | 53.28 |  | 52.63 | 52.5 | 51.41
|  |  | 6A | Academic |  | Massena | 58.45 | 58.46 | 53.17 |  | 54.43 | 54.19 | 54.9
|  |  | 4A | Office-Low-Rise | Office-Low-Rise | NY JFK | 55.31 | 54.34 | 55.56 |  | 49.98 | 53.89 | 51.37
|  |  | 5A | Office-Low-Rise |  | Buffalo | 56.85 | 55.09 | 55.09 |  | 48.56 | 52.62 | 49.93
|  |  | 6A | Office-Low-Rise |  | Massena | 57.78 | 56.23 | 55.38 |  | 48.07 | 52.03 | 51.48
|  |  | 4A | Office-Mid-Rise | Office-Mid-Rise | NY JFK | 55.66 | 56.04 | 51.56 |  | 55.83 | 52.61 | 50.69
|  |  | 5A | Office-Mid-Rise |  | Buffalo | 56.84 | 56.79 | 54.15 |  | 51.86 | 51.28 | 49.67
|  |  | 6A | Office-Mid-Rise |  | Massena | 57.68 | 57.65 | 53.72 |  | 51.93 | 50.67 | 50.99
|  |  | 4A | Grocery | Grocery | NY JFK | 62.31 | 62.37 | 60.48 |  | 60.25 | 61.11 | 69.17
|  |  | 5A | Grocery |  | Buffalo | 61.88 | 61.98 | 58.76 |  | 59.13 | 59.57 | 68.23
|  |  | 6A | Grocery |  | Massena | 61.84 | 61.94 | 59.51 |  | 57.84 | 58.18 | 66.6
|  |  | 4A | Hospital | Hospital | NY JFK | 32.59 | 32.38 | 48.53 |  | 110.8 | 107.7 | 59.06
|  |  | 5A | Hospital |  | Buffalo | 35.69 | 35.69 | 50.58 |  | 91.37 | 93.24 | 58.02
|  |  | 6A | Hospital |  | Massena | 36.89 | 36.83 | 51.21 |  | 78.6 | 79.06 | 57.1
|  |  | 4A | Hotel-Large | Hotel-Large | NY JFK | 54.77 | 55.8 | 56.63 |  | 56.39 | 58.09 | 51.98
|  |  | 5A | Hotel-Large |  | Buffalo | 54.12 | 54.86 | 56.52 |  | 56.04 | 57.88 | 49.34
|  |  | 6A | Hotel-Large |  | Massena | 54.61 | 55.2 | 55.99 |  | 56.03 | 58.19 | 46.39
|  |  | 4A | Hotel-Small | Hotel-Small | NY JFK | 51.22 | 51.3 | 49.87 |  | 48.14 | 54.16 | 50.7
|  |  | 5A | Hotel-Small |  | Buffalo | 48.86 | 49.49 | 48.11 |  | 46.74 | 52.67 | 49.79
|  |  | 6A | Hotel-Small |  | Massena | 48.54 | 48.65 | 47.3 |  | 44.78 | 51.42 | 49.03
|  |  | 4A | Outpatient | Outpatient | NY JFK | 45.4 | 45.93 | 49.46 |  | 130.3 | 141.9 | 57.43
|  |  | 5A | Outpatient |  | Buffalo | 45.77 | 46.37 | 49.62 |  | 119.5 | 122.6 | 55.79
|  |  | 6A | Outpatient |  | Massena | 46.67 | 46.88 | 51.12 |  | 114 | 114.4 | 54.55
|  |  | 4A | Restaurant | Restaurant | NY JFK | 61.84 | 62.24 | 59.51 |  | 57.28 | 59.27 | 52.41
|  |  | 5A | Restaurant |  | Buffalo | 60.52 | 60.48 | 58.46 |  | 57.28 | 59.12 | 52.02
|  |  | 6A | Restaurant |  | Massena | 60.76 | 60.49 | 58.22 |  | 58.24 | 58.63 | 51.39
|  |  | 4A | Retail | Retail | NY JFK | 60.93 | 61.9 | 59.82 |  | 55.06 | 55.1 | 52.06
|  |  | 5A | Retail |  | Buffalo | 60.54 | 61.11 | 58.59 |  | 54.26 | 54.38 | 51.81
|  |  | 6A | Retail |  | Massena | 60.97 | 61.17 | 57.94 |  | 53.45 | 53.17 | 51.43
|  |  | 4A | School | School | NY JFK | 58.76 | 59.75 | 44.1 |  | 55.54 | 56.09 | 48.93
|  |  | 5A | School |  | Buffalo | 56.77 | 58.1 | 43.94 |  | 54.29 | 54.81 | 47.09
|  |  | 6A | School |  | Massena | 59.14 | 59.68 | 50.31 |  | 59.53 | 60.69 | 48.69
|  |  | 4A | Warehouse | Warehouse | NY JFK | 65.67 | 65.87 | 64.07 |  | 52.64 | 52.72 | 49.18
|  |  | 5A | Warehouse |  | Buffalo | 64.15 | 64.19 | 61.68 |  | 50.86 | 50.82 | 48.79
|  |  | 6A | Warehouse |  | Massena | 63.92 | 63.98 | 61.12 |  | 49.24 | 49.1 | 48.7
[6 empty] | Average | 58 |  | 55 |  | 54 |  | 52 |  | Does not include hospital/outpatient; values are outliers
3
Geothermal White Paper: Savings Calculations for Residential Ground Source Heat Pumps: The Basis for Equivalent Full Load Hours (EFLH) and Seasonal Efficiency Factors (2020)
Note on L34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use mid-rise only here so there is a difference between NC and Ex Htg Hours. Existing is expected to have a higher balance pt
Note on O40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Consider Academic cooling hours here too because school BP from ARUP seems very low.

## DOE prototypical models (hidden)
|  | AFTER 1999 | [9 empty] | NEW CONSTRUCTION |  |  |  | Climate 4A
| ASHRAE 90.1 | 2004 | 2004 | 2007 | 2007 | 2010 | 2010 | 2013 | 2013 | 2016 | 2016 | 2019 | 2019 | UNIT | AREA
Building Type |  | BCL | BHL | BCL | BHL | BCL | BHL | BCL | BHL | BCL | BHL | BCL | BHL | BTU/h per ft2 | ft2
Office | 1 | 20.8057 | 16.5942 | 26.0115 | 14.7365 | 21.807 | 11.9398 | 20.342 | 14.0978 | 17.3593 | 11.0788 | 15.4082 | 11.1543
Assembly | 2
Health | 3 | 27.3423 | 9.7597 | 28.7133 | 11.3782 | 28.9475 | 5.3582 | 28.7305 | 5.0269 | 27.816 | 7.9915 | 27.705 | 7.8109
Light Manufacturing | 4
Restaurant | 5 | 78.8449 | 77.466 | 78.8449 | 77.466 | 78.8449 | 77.466 | 78.8449 | 77.466 | 78.8449 | 77.466 | 78.8449 | 77.466
Retail | 6 | 20.8138 | 24.485 | 20.8138 | 24.485 | 20.8138 | 24.485 | 20.8138 | 24.485 | 20.8138 | 24.485 | 20.8138 | 24.485
School | 7 | 14.0535 | 13.6506 | 14.0535 | 13.6506 | 14.0535 | 13.6506 | 14.0535 | 13.6506 | 14.0535 | 13.6506 | 14.0535 | 13.6506
Warehouse | 8 | 2.9972 | 14.4602 | 2.9972 | 14.4602 | 2.9972 | 14.4602 | 2.9972 | 14.4602 | 2.9972 | 14.4602 | 2.9972 | 14.4602
Laboratory | 9
Hotel | 10 | 13.1885 | 4.533 | 13.1885 | 4.533 | 13.1885 | 4.533 | 13.1885 | 4.533 | 13.1885 | 4.533 | 13.1885 | 4.533
Residential | 11 | 7.5611 | 7.8331 | 7.5611 | 7.8331 | 7.5611 | 7.8331 | 7.5611 | 7.8331 | 7.5611 | 7.8331 | 7.5611 | 7.8331
Multifamily | 12 | 11.1734 | 12.956 | 11.1734 | 12.956 | 11.1734 | 12.956 | 11.1734 | 12.956 | 11.1734 | 12.956 | 11.1734 | 12.956
Custom | 13
Large Office |  | 11.8425 | 10.732 | 12.265 | 10.001 | 10.9792 | 8.5224 | 13.1481 | 7.9031 | 12.8566 | 7.5848 | 12.4387 | 7.4254 |  | 498587.9383
Medium Office |  | 11.1218 | 11.674 | 10.4844 | 10.8026 | 11.3372 | 8.3879 | 12.7387 | 8.15 | 12.2497 | 8.0145 | 12.0499 | 6.503 |  | 53627.7949
Small Office |  | 16.5479 | 26.8003 | 16.0468 | 26.4987 | 15.0551 | 24.8283 | 14.9719 | 22.8387 | 22.2004 | 14.3528 | 13.7284 | 21.0927 |  | 5502.0751
MF Mid Rise |  | 7.5568 | 9.5915 | 7.163 | 8.9974 | 6.7497 | 7.1584 | 9.096 | 7.5841 | 8.7546 | 7.5283 | 8.5882 | 7.8055 |  | 33740.6286
MF High Rise |  | 8.19 | 12.7385 | 8.2357 | 11.9265 | 7.9442 | 7.8715 | 10.2495 | 7.0925 | 9.5741 | 7.1341 | 9.2299 | 8.4982 |  | 75991.95
Hospital |  | 12.0043 | 4.0585 | 11.7503 | 4.026 | 10.8382 | 4.1081 | 10.5998 | 3.9021 | 10.6682 | 3.8233 | 10.1805 | 3.7123 |  | 241500.7979
|  | BCL | BHL | BCL | BHL | BCL | BHL | BCL | BHL | BCL | BHL | BCL | BHL
Large Office per Peak Consumption |  | 20.8057 | 16.5942 | 26.0115 | 14.7365 | 21.807 | 11.9398 | 20.342 | 14.0978 | 17.3593 | 11.0788 | 15.4082 | 11.1543 |  | 498587.9383
Small Office per Peak Consumption |  | 14.1712 | 29.0954 | 14.1712 | 29.0954 | 14.1712 | 29.0954 | 14.1712 | 29.0954 | 14.1712 | 29.0954 | 14.1712 | 29.0954 |  | 5502.0751
MF Mid Rise per Peak Consumption |  | 11.2893 | 13.6341 | 10.6517 | 12.8145 | 9.5743 | 10.4504 | 8.4006 | 5.5034 | 8.4942 | 5.5034 | 8.5775 | 5.8835 |  | 30397.0383
MF High Rise per Peak Consumption |  | 11.1734 | 12.956 | 11.1734 | 12.956 | 11.1734 | 12.956 | 11.1734 | 12.956 | 11.1734 | 12.956 | 11.1734 | 12.956 |  | 75991.95
Hospital per Peak Consumption |  | 27.3423 | 9.7597 | 28.7133 | 11.3782 | 28.9475 | 5.3582 | 28.7305 | 5.0269 | 27.816 | 7.9915 | 27.705 | 7.8109 |  | 241500.7979
Quick Service Restaurant |  | 89.8561 | 78.0518 | 89.8561 | 78.0518 | 89.8561 | 78.0518 | 89.8561 | 78.0518 | 89.8561 | 78.0518 | 89.8561 | 78.0518 |  | 2500.8845
Full Service Restaurant |  | 67.8337 | 76.8803 | 67.8337 | 76.8803 | 67.8337 | 76.8803 | 67.8337 | 76.8803 | 67.8337 | 76.8803 | 67.8337 | 76.8803 |  | 5501.9675
Primary School |  | 14.0535 | 13.6506 | 14.0535 | 13.6506 | 14.0535 | 13.6506 | 14.0535 | 13.6506 | 14.0535 | 13.6506 | 14.0535 | 13.6506 |  | 73958.7569
Stand-alone Retail |  | 20.8138 | 24.485 | 20.8138 | 24.485 | 20.8138 | 24.485 | 20.8138 | 24.485 | 20.8138 | 24.485 | 20.8138 | 24.485 |  | 24692.279
Small Hotel |  | 12.3424 | 5.8538 | 12.3424 | 5.8538 | 12.3424 | 5.8538 | 12.3424 | 5.8538 | 12.3424 | 5.8538 | 12.3424 | 5.8538 |  | 40096.4963
Large Hotel |  | 14.0346 | 3.2121 | 14.0346 | 3.2121 | 14.0346 | 3.2121 | 14.0346 | 3.2121 | 14.0346 | 3.2121 | 14.0346 | 3.2121 |  | 122119.567
Warehouse (non-refrigerated) |  | 2.9972 | 14.4602 | 2.9972 | 14.4602 | 2.9972 | 14.4602 | 2.9972 | 14.4602 | 2.9972 | 14.4602 | 2.9972 | 14.4602 |  | 52044.8558
Residential MF CZ4 |  | 6.1708 | 5.2201 | 6.1708 | 5.2201 | 6.1708 | 5.2201 | 6.1708 | 5.2201 | 6.1708 | 5.2201 | 6.1708 | 5.2201 |  | 29404.35
Residential SF CZ4 |  | 8.9514 | 10.4462 | 8.9514 | 10.4462 | 8.9514 | 10.4462 | 8.9514 | 10.4462 | 8.9514 | 10.4462 | 8.9514 | 10.4462 |  | 2377.1
Outpatient Healthcare |  | 41.8575 | 9.5799 | 41.8575 | 9.5799 | 41.8575 | 9.5799 | 41.8575 | 9.5799 | 41.8575 | 9.5799 | 30.0914 | 12.7207 |  | 40945.9832